## Data
name | X2206291 | X7134-C | X656-F | PPE13A
manufacturer | NOJA_01 | NOJA_01 | NOJA_01 | P123
cb_interrupt | 0.1 | 0.1 | 0.1 | 0.1
status | New | New | New | Existing
oc_pu | 2 | 56 | 167 | 352
oc_tms | 0.1 | 0.37 | 0.47 | 0.18
oc_curve | SI | SI | SI | SI
oc_hiset | 1500 | 1700 | 2000 | 2000
oc_min_time | 0.15 | 0.15 | 0.15 | 0.15
oc_hiset2
oc_min_time2
ef_pu | 30 | 30 | 40 | 50
ef_tms | 0.1 | 0.07 | 0.13 | 0.25
ef_curve | SI | SI | SI | SI
ef_hiset |  |  |  | 850
ef_min_time |  |  |  | 0.2
ef_hiset2
ef_min_time2
ct_saturation | 25 | 25 | 25 | 25
ct_error | 10 | 10 | 10 | 10
ct_ratio | 2000 | 2000 | 2000 | 80
rating | 0 | 0 | 0 | 293
load | 109 | 12 | 48 | 164
ds_capacity | 341 | 12 | 152 | 507
max_3p_fl | 2 | 1244 | 1346 | 7812
max_pg_fl | 606 | 617 | 654 | 1723
min_2p_fl | 639 | 582 | 675 | 997
min_pg_fl | 333 | 331 | 363 | 460
max_tr_size | 500 | 100 | 315 | 750
max_tr_fuse | 40Kmax | 25Kmax | 40Kmax | 500_50A_Oil
tr_max_3p | 829 | 971 | 887 | 7595
tr_max_pg | 425 | 491 | 473 | 1711
downstream_devices | 0 | 0 | X7134-C | X2206291, X656-F
upstream_devices | PPE13A | X656-F, PPE13A | PPE13A
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should be a drop-down list
Note on A19: Dan Park: Dan Park: Relay CT saturation factor
Note on A20: Dan Park: Dan Park: Maximum CT ratio error (%). Equal to CT
Note on A22: Dan Park: Dan Park: Section conductor 2HR rating. If 0, this isn't a feeder relay
Note on A23: Dan Park: Dan Park: Would this be the five year 10% POE peak load?
Note on A24: Dan Park: Would this be the five year 10% POE peak load?
Note on A30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should be a drop-down list
Note on A33: Dan Park: Dan Park: List of all downstream devices backed up by this relay